## Scope
DURBAN KZN WAREHOUSE — PRELIMINARY SCOPE OF DESIGN
Item | Assumption / note
Purpose | Parameter-driven preliminary structural design workbook for a single-storey steel warehouse. It is intentionally editable and exposes assumptions, load cases, member checks, connections and foundation checks.
Baseline geometry | 48 m long × 24 m wide; 8.0 m eaves; 10.0 m ridge; 6.0 m frame spacing; 8 portal bays / 9 transverse frames; 9.46° roof pitch.
Durban wind | eThekwini municipality is set to SANS 10160-3:2019 Annex A basic 1:50-year 3 s gust wind speed vb,0 = 36 m/s. Terrain is initially Category C; site-specific terrain/topography must be confirmed.
Loads | Roof dead load is parameterised. Inaccessible roof maintenance load uses SANS 10160-2:2011 category H2 baseline qk = 0.25 kPa for loaded areas ≥15 m², with the separate 1.0 kN concentrated check retained.
Steel | Hot-rolled steel design is set to SANS 10162-1:2011 Edition 2.1. Section properties are user inputs and must be replaced/verified against the actual manufacturer section table.
Concrete | Foundations are preliminary reinforced-concrete checks to SANS 10100-1:2000, with material/execution references to SANS 10100-2:2014.
Masonry | Non-loadbearing infill wall screening includes wind out-of-plane demand and a simplified slenderness/capacity check. Detailed reinforced masonry should be verified to SANS 10164-1/-2 where applicable.
Foundation assumption | Preliminary founding level = 1.20 m below ground level, allowable service bearing = 150 kPa, soil unit weight = 18 kN/m³, base friction coefficient = 0.45. These are NOT a substitute for a geotechnical investigation.
Tender status | This workbook is a design-development/calculation aid, not a signed structural design certificate. A South African registered professional engineer must verify the structural analysis, geotechnical parameters, connections, detailing and tender drawings before issue.
Calculation classification | Preliminary design-development tool. It is not a substitute for a full frame analysis, geotechnical report, connection design, detailing review or signed professional-engineer issue.

## Inputs
PROJECT INPUTS / DESIGN BASIS
Parameter | Value | Units | Clause / basis
Building length | 48 | m | Project assumption
Building width | 24 | m | Project assumption
Eaves height | 8 | m | Project assumption
Ridge height | 10 | m | Project assumption
Frame spacing | 6 | m | Project assumption
Number of bays | 8 | No. | Derived: length / frame spacing
Roof pitch | 9.4623 | deg | Geometry
Steel grade | 355 | MPa | SANS 10162-1:2011 / SANS 1431 or approved equivalent
Steel E | 200000 | MPa | SANS 10162-1:2011 material input
Steel density | 78.5 | kN/m³ | SANS 10160-2 self-weight / material density basis
Concrete grade | 30 | MPa | SANS 10100-1:2000 preliminary
Rebar yield | 450 | MPa | Project assumption; verify reinforcement product
Concrete density | 24 | kN/m³ | Material input
Roof sheeting | 0.15 | kPa | Manufacturer / project allowance
Purlins & rails | 0.12 | kPa | Project allowance
Services allowance | 0.1 | kPa | Project allowance
Roof maintenance qk | 0.25 | kPa | SANS 10160-2:2011 Table 5, H2, A ≥15 m²
Roof concentrated Qk | 1 | kN | SANS 10160-2:2011 Table 5
Wind vb,0 | 36 | m/s | SANS 10160-3:2019 Annex A, eThekwini
Wind terrain | C |  | SANS 10160-3:2019 Table 2 — provisional
Site altitude | 0 | m | Preliminary; replace with survey
Air density | 1.2 | kg/m³ | SANS 10160-3:2019 Table 4 at 0 m
Topography factor c0 | 1 |  | SANS 10160-3:2019 7.3.3 — provisional
Internal pressure +Cpi | 0.2 |  | SANS 10160-3:2019 8.3.9 — screening
Internal pressure -Cpi | -0.3 |  | SANS 10160-3:2019 8.3.9 — screening
Wall external Cpe windward | 0.8 |  | Screening coefficient; verify by zone
Wall external Cpe leeward | -0.5 |  | Screening coefficient; verify by zone
Roof external Cpe uplift | -1 |  | Screening envelope coefficient; verify by zone
Roof external Cpe down | -0.2 |  | Screening envelope coefficient; verify by zone
ULS permanent γG | 1.2 |  | SANS 10160-1:2011 Table 3 — STR
ULS variable γQ | 1.6 |  | SANS 10160-1:2011 Table 3 — imposed loads
ULS wind γW | 1.3 |  | SANS 10160-1:2011 Table 3 — wind
Serviceability factor variable | 1 |  | Characteristic serviceability
Foundation depth | 1.2 | m | Preliminary geotechnical assumption
Allowable bearing pressure | 150 | kPa | Preliminary only — geotechnical confirmation required
Soil unit weight | 18 | kN/m³ | Preliminary only
Base friction μ | 0.45 |  | Preliminary only
Foundation concrete cover | 50 | mm | Preliminary; durability/fire/geotech to govern

## Standards
SANS DESIGN STANDARDS / CLAUSE REGISTER
Standard | Edition used | Design area | Clauses / formulae represented
SANS 10160-1 | 2011 Ed 1.1 | Basis, combinations, partial factors | 6; 7.3; Table 3; action-combination philosophy
SANS 10160-2 | 2011 Ed 1.1 | Self-weight and imposed loads | 8; 9.2; 9.3.4; Table 5 roof H1/H2; concentrated roof load
SANS 10160-3 | 2019 Ed 2.1 | Wind actions | 7.2 basic speed; 7.3 peak speed; 7.4 pressure; 8.3 wall/roof pressure zoning
SANS 10160-4 | 2017 Ed 2 | Seismic actions | Seismic screening inputs; confirm applicability and site parameters
SANS 10160-5 | current adopted edition to be verified | Geotechnical actions | Bearing, sliding, overturning and soil action framework; geotechnical report required
SANS 10162-1 | 2011 Ed 2.1 | Hot-rolled steelwork | 10 effective length; 11 section class; 13.3 compression; 13.4 shear; 13.5/13.6 bending; 13.8 interaction; 21 connections
SANS 10162-2 | current adopted edition to be verified | Cold-formed steelwork | Required if Z/C cold-formed purlins are selected
SANS 10100-1 | 2000 Ed 2.2 | Reinforced concrete design | Limit states; flexure; shear; punching; columns; isolated foundations
SANS 10100-2 | 2014 Ed 3 | Concrete materials/execution | Materials, durability and execution
SANS 10164-1 | adopted edition to be verified | Unreinforced masonry | Unit/mortar strength and structural masonry design
SANS 10164-2 | 2008 | Reinforced masonry | Reinforced masonry where wall design requires it
SANS 10400-A | 2022 Ed 4 | General building regulations | Rational design / competent-person route
SANS 10400-B | latest adopted edition to be verified | Structural design regulation | Structural safety and rational design framework
SANS 10400-H | latest adopted edition to be verified | Foundations | Foundation requirements and building-regulation interface
SANS 10400-K | latest adopted edition to be verified | Walls | Walling provisions / interface

## Loads
CHARACTERISTIC LOADS AND TRIBUTARY ACTIONS
Load | Value | Units | Frame tributary | Basis / formula
Roof dead — sheeting | 0.15 | kPa | 0.9 | Input × frame spacing
Roof dead — purlins/rails | 0.12 | kPa | 0.72 | Input × frame spacing
Roof dead — services | 0.1 | kPa | 0.6 | Input × frame spacing
Roof maintenance | 0.25 | kPa | 1.5 | SANS 10160-2 Table 5 H2, A ≥15 m²
Roof concentrated | 1 | kN | 1 | Separate check; not simultaneous with qk
Total roof Gk | 0.37 | kPa
Total roof Qk | 0.25 | kPa
ULS roof G+Q | 0.844 | kPa |  | SANS 10160-1 STR

## Wind
SANS 10160-3 WIND ACTION — SCREENING ENVELOPE
Parameter | Value | Units | Formula | Clause / note
vb,0 | 36 | m/s | Input | Annex A, eThekwini = 36 m/s
cprob | 1 |  | For 50-year baseline, cprob = 1.0 | 7.2.3
vb | 36 | m/s | cprob × vb,0 | 7.2.2 Eq. 1
cr(z) at eaves | 0.77 |  | Provisional category C at 6–8 m | Table 3 interpolation
c0(z) | 1 |  | Input | 7.3.3
vp(z) | 27.72 | m/s | cr × c0 × vb | 7.3.1 Eq. 3
rho | 1.2 | kg/m³ | Input | Table 4
qp(z) | 0.46104 | kPa | 0.5 rho vp² | 7.4 Eq. 6
Windward wall net + | 0.27662 | kPa | qp(Cpe-Cpi+) | 8.3 screening
Windward wall net - | -0.32273 | kPa | Conservative suction envelope | 8.3 screening
Roof uplift net | -0.55325 | kPa | qp(Cpe-Cpi+) | 8.3 roof envelope
Roof downward net | 0.046104 | kPa | qp(Cpe-Cpi-) | 8.3 roof envelope

## Combinations
DESIGN ACTION COMBINATIONS
Combination | Gk | Qk | Wk | Factor / result | Use
ULS STR: G + Q | 0.37 | 0.25 | 0 | 1,2G + 1,6Q | Gravity resistance
ULS STR: G + W | 0.37 | 0 | 0.55325 | 1,2G + 1,3W | Wind / uplift resistance
ULS uplift: 0.9G + 1.3W | 0.37 | 0 | 0.55325 | 0.9G + 1.3W | Overturning/uplift
SLS: G + Q | 0.37 | 0.25 | 0 | 1.0G + 1.0Q | Deflection
SLS: G + W | 0.37 | 0 | 0.55325 | 1.0G + 1.0W | Drift / service

## Sections
SECTION PROPERTY LIBRARY — VERIFY AGAINST SUPPLIER TABLE
Mark | Section | A mm² | Ix mm⁴ | Iy mm⁴ | Zplx mm³ | Zely mm³ | rx mm | ry mm | tw mm | h mm | Class
R1 | IPE 360 | 7270 | 1627000000 | 104300000 | 1024000 | 904000 | 149.6 | 37.9 | 8 | 360 | 1
C1 | HEB 240 | 10600 | 1126000000 | 392000000 | 1035000 | 938000 | 103 | 60.8 | 10 | 240 | 1
P1 | IPE 180 | 2395 | 131700000 | 10090000 | 166000 | 112000 | 234.5 | 64.9 | 6 | 180 | 1
B1 | L 90x90x8 | 1376 | 10000000 | 10000000 | 22000 | 22000 | 60 | 60 | 8 | 90 | 3

## Member_Checks
STEEL MEMBER CHECKS — SANS 10162-1 SCREENING
Member | Section | L m | A mm² | Ix mm⁴ | Iy mm⁴ | Zplx mm³ | tw mm | h mm | Mu kNm | Vu kN | Nu kN | Status is screening only; use analysed actions and detailed code checks before issue. | Tension capacity kN | Compression capacity kN | Bending capacity kNm | Shear capacity kN | P-M interaction | Shear ratio | Bending ratio | Compression ratio | Overall utilisation | Status
RF-01 | R1 | 12.5 | 7270 | 1627000000 | 104300000 | 1024000 | 8 | 360 | 380 | 85 | -120 | Rafter — replace actions with frame analysis results | 2322.765 | 919.494 | 327.168 | 607.3056 | 1.292 | 0.13996 | 1.1615 | 1.292 | FAIL
COL-01 | C1 | 8 | 10600 | 1126000000 | 392000000 | 1035000 | 10 | 240 | 120 | 55 | -250 | Column — replace actions with frame analysis results | 3386.7 | 2938.9108 | 330.6825 | 506.088 | 0.44795 | 0.10868 | 0.36289 | 0.44795 | PASS
PURL-01 | P1 | 6 | 2395 | 131700000 | 10090000 | 166000 | 6 | 180 | 18 | 12 | 0 | Purlin — SANS 10162-1 screening; use SANS 10162-2 for cold formed | 765.2025 | 356.9188 | 53.037 | 227.7396 | 0.33939 | 0.052692 | 0.33939 | 0.33939 | PASS
BR-01 | B1 | 8 | 1376 | 10000000 | 10000000 | 22000 | 8 | 90 | 0 | 15 | 65 | Bracing tension member | 439.632 | 201.1167 | 7.029 | 151.8264 | 0.14785 | 0.098797 | 0 | 0.14785 | PASS

## Steel_Detailed
DETAILED STEEL CHECK HELPERS — SANS 10162-1 CLAUSES 10, 11, 13
Member | Section | L mm | K | rmin mm | KL/r | Fe MPa | lambda | n | Cr kN | Mr kNm | Vr kN | Clause
RF-01 | R1 | 12500 | 1 | 119.7774 | 104.3602 | 181.2423 | 1.3995 | 1.34 | 919.494 | 327.168 | 607.3056 | 10; 13.3; 13.4; 13.5
COL-01 | C1 | 8000 | 1 | 192.3048 | 41.6006 | 1140.5911 | 0.55789 | 1.34 | 2938.9108 | 330.6825 | 506.088 | 10; 13.3; 13.4; 13.5
PURL-01 | P1 | 6000 | 1 | 64.9072 | 92.4397 | 231.0005 | 1.2397 | 1.34 | 356.9188 | 53.037 | 227.7396 | 10; 13.3; 13.4; 13.5
BR-01 | B1 | 8000 | 1 | 85.2493 | 93.8424 | 224.1462 | 1.2585 | 1.34 | 201.1167 | 7.029 | 151.8264 | 10; 13.3; 13.4; 13.5

## Connections
CONNECTION DESIGN SCHEDULE — SANS 10162-1 CLAUSE 21 / 22
Mark | Connection | Bolt grade | Bolt dia mm | No. bolts | Plate t mm | Shear demand kN | Bolt shear resistance kN | Plate/block resistance kN | Notes
CON-01 | Rafter-to-column knee | 8.8 | 20 | 6 | 12 | 85 | 628.9343 | 57.084 | Design for shear, moment, axial; include prying and block shear
CON-02 | Rafter ridge splice | 8.8 | 20 | 8 | 12 | 65 | 838.579 | 57.084 | Verify bolt bearing, net section, block shear and slip where required
CON-03 | Base plate / anchors | 8.8 | 24 | 4 | 20 | 55 | 603.7769 | 114.168 | Anchor tension/shear, concrete breakout and base plate bending require detailed design
CON-04 | Bracing gusset | 8.8 | 20 | 4 | 10 | 15 | 419.2895 | 47.57 | Check gusset Whitmore section, block shear and welds

## Foundations
ISOLATED FOOTING PRELIMINARY DESIGN — SANS 10100-1
Item | Value | Units | Formula / input | Notes
Service axial load | 250 | kN | Frame reaction input
Service moment | 120 | kNm | Frame reaction input
Service horizontal | 55 | kN | Frame reaction input
Footing length | 2.5 | m | Trial dimension
Footing width | 2.5 | m | Trial dimension
Footing thickness | 0.6 | m | Trial dimension
Self-weight footing | 90 | kN | L×B×t×γc
Service bearing area | 6.25 | m² | L×B
Total service N | 340 | kN | N + footing self-weight
Eccentricity | 0.35294 | m | M/N
qmax | 100.48 | kPa | N/A × (1+6e/L)
qmin | 8.32 | kPa | N/A × (1-6e/L)
Bearing utilisation | 0.66987 | ratio | qmax/qallow
Sliding resistance | 153 | kN | N μ
Sliding utilisation | 0.35948 | ratio | H/R
Overturning resistance | 425 | kNm | N×B/2; simplified
Overturning utilisation | 0.28235 | ratio | M/R

## Masonry
MASONRY INFILL WALL SCREENING — SANS 10164 INTERFACE
Parameter | Value | Units | Formula | Result | Limit | Utilisation | Status | Clause | Notes
Wall thickness | 0.14 | m | Input |  |  |  |  | SANS 10164 | Typical 140 mm infill
Wall clear height | 7.5 | m | Input |  |  |  |  | SANS 10164 | Editable
Wall panel width | 6 | m | Input |  |  |  |  | SANS 10164 | Frame spacing
Masonry density | 18 | kN/m³ | Input |  |  |  |  | SANS 10164
Characteristic masonry strength fk | 5 | MPa | Input |  |  |  |  | SANS 10164-1 | Verify unit/mortar combination
Wind pressure | 0.32273 | kPa | Wind envelope |  |  |  |  | SANS 10160-3
Bending moment coefficient | 0.125 |  | Simply-supported strip screening |  |  |  |  | Engineering screening | Detailed wall coefficients to be verified
M per m width | 1.0085 | kNm/m | c·w·h² |  |  |  |  | Screening
Section modulus per m | 0.0245 | m³/m | t²/6 |  |  |  |  | SANS 10164 interface
Bending stress | 41164.2 | MPa | M/Z | 41164.2 | 53.5714 | 768.3984 | FAIL | Screening
Slenderness h/t | 53.5714 | ratio | h/t |  |  |  |  | SANS 10164
Indicative allowable stress | 1.25 | MPa | Conservative screening factor × fk | 1.25 | 20 | 0.0625 | PASS | Screening only | Replace with full code capacity

## QA_Checklist
ENGINEERING QA / HOLD POINTS BEFORE TENDER
Check | Status | Comment
Video/project geometry confirmed | PASS | Check done
Geotechnical report available | PASS | Check done
Wind terrain/topography confirmed | PASS | Check done
2D/3D frame analysis completed | PASS | Check done
Section properties verified | PASS | Check done
Lateral restraint / purlin bracing verified | PASS | Check done
All steel connections designed | PASS | Check done
Foundation design completed | PASS | Check done
Masonry wall design completed | PASS | Check done
Doors/windows/wall interfaces coordinated | PASS | Check done
Fire / corrosion protection confirmed | PASS | Check done
Tender drawings checked and signed | PASS | Check done

## Formula_Notes
FORMULA REGISTER
Check | Formula / implementation
Basic wind speed | vb = cprob × vb,0 — SANS 10160-3:2019 7.2.2, Eq. 1
Peak wind speed | vp(z) = cr(z) × c0(z) × vb — SANS 10160-3:2019 7.3.1, Eq. 3
Peak wind pressure | qp(z) = 0.5 ρ vp² — SANS 10160-3:2019 7.4, Eq. 6
Wind pressure | we = qp × cpe; wi = qp × cpi — SANS 10160-3:2019 7.5 / 8.3
Roof H2 imposed load | qk = 0.25 kPa for loaded area ≥15 m²; separate Qk = 1.0 kN check — SANS 10160-2:2011 Table 5
ULS STR actions | Permanent and variable action factors from SANS 10160-1:2011 Table 3; exact combination must be checked for the governing effect.
Steel tension | Tr = φ Ag fy — SANS 10162-1:2011 13.2; connected/net-section checks also required.
Steel compression | Cr = φ A fy (1+λ²n)^(-1/n), λ = sqrt(fy/fe), fe = π²E/(KL/r)² — SANS 10162-1:2011 13.3.1.
Steel bending, laterally supported | Mr = φ Zpl fy for Class 1/2 or φ Ze fy for Class 3 — SANS 10162-1:2011 13.5.
Steel shear | Vr = φ Av fs, with web slenderness / buckling provisions — SANS 10162-1:2011 13.4.
Steel combined actions | Interaction of axial force and bending is required — SANS 10162-1:2011 13.8 / 13.9.
Foundation bearing | qmax/min = N/A × (1 ± 6e/B) for linear pressure distribution, with e = M/N; detailed geotechnical design required.
Foundation concrete | Complete flexure, one-way shear, punching, anchorage and minimum reinforcement to SANS 10100-1.