## gravity pipe flow
Document Summary: Initial Design Assumptions & Hydraulics
Title: Technical Specification & Design Assumptions: Gravity Sewer & Pressure Pipe Reticulation
Scope: Hydraulic design basis for partial-depth gravity pipe rating curves
Gravity Pipe Flow Calculator (Manning's Equation)
Parameter | Value | Unit | Description
Pipe Diameter (D) | 2 | m | Internal diameter (Concrete Pipe)
Pipe Slope (S) | 0.006 | m/m | Bed slope
Manning's n | 0.013 | - | Roughness coefficient
Full Flow Area (A_full) | 3.1416 | m^2 | Full Flow Area
Full Hydraulic Radius (R_full) | 0.5 | m | Full Hydraulic Radius
Full Flow Rate (Q_full) | 11.7922 | m^3/s | Full Flow Rate
Full Flow Rate (Q_full L/s) | 11792.2175 | L/s | Full Flow Rate
Full Flow Velocity (V_full) | 3.7536 | m/s | Full Flow Velocity
Gravity Flow Rating Table (Partial Depth Flow)
d/D Ratio | Flow Depth d (m) | Theta (rad) | Wetted Area A (m2) | Wetted Perimeter P (m) | Hydraulic Radius R (m) | Flow Rate Q (m3/s) | Flow Rate Q (L/s) | Velocity V (m/s)
0.1 | 0.2 | 1.287 | 0.1635 | 1.287 | 0.026022 | 0.13222 | 132.2208 | 0.80868
0.2 | 0.4 | 1.8546 | 0.4473 | 1.8546 | 0.071189 | 0.5742 | 574.1956 | 1.2837
0.3 | 0.6 | 2.3186 | 0.79267 | 2.3186 | 0.12616 | 1.3334 | 1333.3804 | 1.6821
0.4 | 0.8 | 2.7389 | 1.1735 | 2.7389 | 0.18677 | 2.3913 | 2391.2648 | 2.0378
0.5 | 1 | 3.1416 | 1.5708 | 3.1416 | 0.25 | 3.7143 | 3714.3158 | 2.3646
0.6 | 1.2 | 3.5443 | 1.9681 | 3.5443 | 0.31323 | 5.2553 | 5255.2886 | 2.6702
0.7 | 1.4 | 3.9646 | 2.3489 | 3.9646 | 0.37384 | 6.951 | 6950.9749 | 2.9592
0.8 | 1.6 | 4.4286 | 2.6943 | 4.4286 | 0.42881 | 8.7153 | 8715.3428 | 3.2347
0.9 | 1.8 | 4.9962 | 2.9781 | 4.9962 | 0.47398 | 10.4203 | 10420.2625 | 3.499
1 | 2 | 6.2832 | 3.1416 | 6.2832 | 0.5 | 11.7922 | 11792.2175 | 3.7536

## Pressure Pipe Flow System Curve
Pressure Pipe Flow System Curve Calculator (Hazen-Williams & Minor Losses)
Parameter | Value | Unit | Description
Pipe Length (L) | 750 | m | Total length of pipeline
Pipe Diameter (D) | 0.5 | m | Internal diameter
Hazen-Williams C | 130 | - | Roughness coefficient
Static Head (H_static) | 20 | m | Elevation lift / pressure differential
Minor Loss Sum (K_sum) | 2.6 | - | Fitting & valve loss coefficients
Gravitational Acc (g) | 9.81 | m/s2 | Acceleration due to gravity
Pipe Cross-Area (A) | 0.19635 | m^2 | Area
Pressure Pipe System Curve Table
Flow Rate Q (L/s) | Flow Rate Q (m3/s) | Velocity V (m/s) | Friction Loss Hf (m) | Minor Loss Hm (m) | Total Head Loss H_loss (m) | Total Dynamic Head TDH (m)
0 | 0 | 0 | 0 | 0 | 0 | 20
10 | 0.01 | 0.05093 | 0.0056262 | 0.00034373 | 0.00597 | 20.006
20 | 0.02 | 0.10186 | 0.020311 | 0.0013749 | 0.021686 | 20.0217
30 | 0.03 | 0.15279 | 0.043038 | 0.0030935 | 0.046131 | 20.0461
40 | 0.04 | 0.20372 | 0.073322 | 0.0054996 | 0.078822 | 20.0788
50 | 0.05 | 0.25465 | 0.11084 | 0.0085932 | 0.11944 | 20.1194
60 | 0.06 | 0.30558 | 0.15537 | 0.012374 | 0.16774 | 20.1677
70 | 0.07 | 0.35651 | 0.2067 | 0.016843 | 0.22354 | 20.2235
80 | 0.08 | 0.40744 | 0.26469 | 0.021999 | 0.28669 | 20.2867
90 | 0.09 | 0.45837 | 0.32921 | 0.027842 | 0.35705 | 20.3571
100 | 0.1 | 0.5093 | 0.40015 | 0.034373 | 0.43452 | 20.4345